## Slide 1: COMP1: Heat balance compressor – suction superheater 27.08.2020
COMP1 issue: is condensing capacity correct?

## Slide 2: COMP1: Heat balance compressor – suction superheater 27.08.2020

## Slide 3: COMP1: Heat balance compressor – suction superheater 27.08.2020
COMP1 (tb0285/06.05.88):
Qe = (H1_hx – H4) x g = 859 kW
W = (H2 – H1) x g = 170 kW
Qc = (H3_hx – H2) x g = 1088 kW - NO
Correct Qc:
Qc = (H3 – H2) x g = 1022 kW